Battery Charging Room Application

Provide a wall mount, programmable 4-ch controller model QCC-M with back-lit LCD digital display, LED alarm indication, 80 dB audible alarm with silence / acknowledge button integrated into the Lexan label all housed in a rugged, water/dust tight IP54 rated polycarbonate/ABS enclosure with secured, hinged door. The controller shall have real time display of gas concentration, and alarm status. Controller shall be capable of supporting up to four remote sensor/transmitters. Controller shall provide three dry contact relays rated 5 A @ 240VAC SPDT each for control of other devices. If information is required at a DDC/BMS the QCC comes standard with Modbus output or “optional” BACnet® output communications protocol. Two “optional” analog output signals are also available if desired. Controller wiring to remote sensor/transmitter shall be 3-conductor, 16-18 gauge, and stranded, shielded in conduit. System power requirement is 90 to 240 VAC, 47 to 63 Hz or low voltage 16-30VDC or 12-28 VAC. The controller shall be tested to CSA/UL/CE, FCC and IP54 standards. Controller shall be installed at 4’ to 6’ from the floor in an area visible to anyone entering in the room.

Provide two remote mount transmitters model LPT-A-CH2-100 with accurate catalytic combustible sensor with measurement range of 0-100% LEL. The sensor shall be housed in a rugged, wall mount, IP54 rated, water/dust tight ABS/polycarbonate junction box. The remote mount sensor/transmitter shall operate on power supplied by the QCC control panel, and shall provide an analog output signal (4-20 mA) to the control panel. Install the LPT-A-CH2 sensor on or near the ceiling as H2 (hydrogen) is much lighter than air. The sensor/transmitter shall be tested to CSA/UL/CE, FCC and IP54 standards.

Provide two remote strobe-horn alarm devices model RSH-24V-R.

System operation shall be as follows: Upon detection of 10% LEL H2, the system shall illuminate the Low alarm LED, and the Low alarm relay controlling the low speed of roof top fan starters.

Upon detection of 20% LEL H2, the system shall illuminate the High alarm LED and remote mounted alarms RSH-24V-R, and activate the High alarm relay controlling high speed of roof top fan starters.

The contractor shall provide all wiring (analog), conduit and interconnection required for a successful installation. Wiring must be 16-18 gauge, stranded, shielded and preferably in conduit. System shall be tested and commissioned after installation by a trained, authorized service representative of the manufacturer, with a detailed service report provided after the site visit.

Approved manufacturer:

Critical Environment Technologies Canada Inc.

Reference: 20190422-03