Carbon Monoxide (CO) & Methane (CH4) Detection for Boiler Room Applications

Provide a wall mount, self-contained detector model DCC-A-TCO-R with integral electrochemical CO sensor, back-lit LCD digital display, LED alarm indication, and 80 dB audible alarm with silence / acknowledge button integrated into the Lexan label all housed in a rugged, water/dust tight IP54 rated polycarbonate/ABS enclosure with secured, hinged door. The controller shall have real time display of gas concentration, and alarm status.  Controller shall be capable of supporting one remote methane sensor for the detection of leaked natural gas. Controller shall provide two 4-20 mA analog outputs for input to a DDC or data/trend logging device. Controller shall provide two dry contact relays rated 5 A @ 240VAC SPDT each for control of other devices. Controller wiring to remote sensor/transmitter shall be 3-conductor, 16-18 gauge, and stranded, shielded in conduit. System power requirement is 90 to 240 VAC, 47 to 63 Hz or low voltage 16-30VDC or 12-28 VAC. The controller shall be tested to CSA/UL/CE, FCC and IP standards. Controller shall be installed inside boiler room at 4’ to 6’ from the floor in an area visible to anyone working in the room and in relation to potential boiler leak areas for exhaust gas containing carbon monoxide.

Provide one remote mount sensor model LPT-A-CCH4-100 for methane (natural gas) with catalytic combustible sensor with a detection range of 0 – 100% LEL. The sensor shall be housed in a rugged, wall mount, ABS/polycarbonate junction box. The remote mount sensor shall operate on power supplied by the control panel, and shall provide an analog output signal to the control panel. Install the CH4 sensor on or near the ceiling in an area over where incoming natural gas pipes conjunct with the boiler (natural gas is much lighter than air). The LPT-A should be installed no more than 300’ away from the DCC-D-TCO-R detector.

System operation shall be as follows: Upon detection of 25 ppm CO or 10% LEL CH4, the system shall illuminate the Low alarm LED and the Low alarm relay controlling the exhaust fan starter. The system shall keep the exhaust fan operational until the level of CO or Methane drops below the alarm threshold. Upon detection of 100 ppm CO or 20% LEL CH4, the system shall illuminate the High alarm LED and the High alarm relay will be activated controlling anything connected to it. The system shall keep the High relay active until the level of CO or Methane drops below the alarm threshold. The audible alarm shall be activated at High alarm level and can be silenced from the integrated silence button on the DCC label. Any remote alarm devices shall be activated at this alarm level as well. The DCC controller system will continuously output two 4-20 mA signals representing the real time values of any CO and CH4 gases whether or not they are connected to a data recording device.

The contractor shall provide all wiring (analog), conduit and interconnection required for a successful installation. Wiring must be 16-18 gauge, stranded, shielded and preferably in conduit. System shall be tested and commissioned after installation by a trained, authorized service representative of the manufacturer, with a detailed service report provided after the site visit.

Approved manufacturer:

Critical Environment Technologies Canada Inc.

Reference: 20190422-01