Airport Exhaust and Jet Fuel Monitoring

Provide a wall mount, programmable 4-ch controller model QCC-M-L with back-lit LCD digital display, LED alarm indication, top mounted strobe light, 80 dB audible alarm with silence / acknowledge button integrated into the Lexan label all housed in a rugged, water/dust tight IP54 rated polycarbonate/ABS enclosure with secured, hinged door. The controller shall have real time display of gas concentration, and alarm status. Controller shall be capable of supporting up to four remote sensor/transmitters. Controller shall provide three dry contact relays rated 5 A @ 240VAC SPDT each for control of other devices. If information is required at a DDC/BMS the QCC comes standard with Modbus output or “optional” BACnet output communications protocol. Two “optional” analog output signals are also available if desired. Controller wiring to remote sensor/transmitter shall be 3-conductor, 16-18 gauge, and stranded, shielded in conduit. System power requirement is 90 to 240 VAC, 47 to 63 Hz or low voltage 16-30VDC or 12-28 VAC. The controller shall be tested to CSA/UL/CE, FCC and IP54 standards. Controller shall be installed outside entrance door to mechanical room at 4’ to 6’ from the floor in an area visible to anyone entering in the room.

Provide two remote mount transmitters model LPT-TCO with accurate electrochemical Carbon Monoxide sensor with measurement range of 0-200 ppm. The sensor shall be housed in a rugged, wall mount, ABS/polycarbonate junction box. The remote mount sensor/transmitter shall operate on power supplied by the QCC control panel, and shall provide an analog output signal (4-20 mA) to the control panel. Install the LPT-TCO sensor 4’ to 6” from the floor (breathing zone). CO is slightly lighter than air. The sensor/transmitter shall be tested to CSA/UL/CE, FCC and IP54 standards

Provide two remote mount transmitters model LPT-A-R/ESH-A-JET with remote infrared sensor calibrated for jet fuel with measurement range of 0-100% LEL. The transmitter & sensor shall be housed in separate rugged, wall mount, ABS/polycarbonate, water/dust tight junction box with hinged, secured door. Mount the transmitter portion (LPT-A-R) 4’ to 6’ from the floor so display is visible at worker height and mount the remote infrared sensor (ESH-A) 12” from the floor. The sensor/transmitter shall operate on power supplied by the QCC control panel, and shall provide an analog output signal to the control panel. The sensor/transmitter shall be tested to CSA/UL/CE, FCC and IP54 standards

System operation shall be as follows: Upon detection of 25 ppm or 10% LEL flammable jet fuel, the system shall illuminate the Low alarm LED and top mounted strobe light on the QCC, and the Low alarm relay controlling the exhaust fan starter.

Upon detection of 100 ppm CO or 20% LEL flammable jet fuel, the system shall illuminate the High alarm LED and top mounted strobe light on the QCC, and activate the High alarm relay.

The contractor shall provide all wiring (analog), conduit and interconnection required for a successful installation. Wiring must be 16-18 gauge, stranded, shielded and preferably in conduit. System shall be tested and commissioned after installation by a trained, authorized service representative of the manufacturer, with a detailed service report provided after the site visit.

Approved manufacturer:

Critical Environment Technologies Canada Inc.